## Input Sheet
DEAP Heat Pump Tool | [6 empty] | I.S. EN 14825 | Yes | Space heating | Air to Water | Heat Emission Type | Fuel |  | Fixed Outlet | Yes | NA | No Hot Water Store | 3XS | ERROR | 0 | 8 | Water heating energy efficiency, ηwh
Version 1 | [6 empty] | I.S. EN 14511 | No | Domestic Hot Water | Brine to Water | 1 or more Radiators present | Electricity | 2.19 | Variable Outlet | No | Low Temperature | Integral Hot Water Storage | XXS |  | 0 | 16 | Coefficient of Performance, COP
Publication Date: Q1 2016 | [6 empty] | I.S. EN 255-3 |  | Space heating and Domestic Hot Water | Water to Water | Fan Coil Units present (no radiators) | Mains Gas | 1.1 |  |  | High Temperature | Separate Hot Water Storage | XS |  | 0 | 24
Description: | Value: | Unit: | Guidance Notes: |  |  |  | I.S. EN 16147 |  |  | Exhaust Air to Water | Underfloor heating only | LPG Gas (bottled or bulk) | 1.1 |  |  | Very High Temperature | Integral and separate Hot Water Storage | S
[10 empty] | Air to Air | Air | Heating Oil | 1.1 |  |  |  |  | M
1. General information | [9 empty] | Brine to Air |  | Biodiesel from renewable sources only | 1.3 |  |  |  |  | L
Name of owner/ client: | [9 empty] | Water to Air |  | Bioethanol from renewable sources only | 1.34 |  |  |  |  | XL
Address of installation: | [11 empty] | House coal/ Anthracite | 1.1 |  |  |  |  | XXL
MPRN Number: | [11 empty] | manufactured smokeless fuel | 1.2 |  |  |  |  | 3XL
Eircode: | [11 empty] | Peat | 1.1 |  |  |  |  | 4XL
BER Number: | [11 empty] | Wood logs/pellets/chips | 1.1
2. Assessor Details | [11 empty] | Solid multi-fuel | 1.1
Assessor Name:
Assessor Number:
3. Building Data
Total heat loss (W/K) taken from DEAP |  | W/K | Source from the Building Elements - Heat Loss Results Tab in DEAP
Heat Loss Watts | #VALUE! | Watts | Required Heating Capacity at design conditions.
Is the Heat Pump part of a Group Heating Scheme | No
Proportion of group heating provided by the heat pump | 0% | %
Floor Area of Dwelling | 0 | m2 | Source from DEAP
If Heat Pump serves a Group Heat Scheme, the total Floor Area served by Heat Pump is: | 0 | m2
4. Heat pump Data
Manufacturer of the installed heat pump(s) | Viessmann |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology
Model of the installed heat pump(s) | Vitocal 200 AWOT-M-E 201.08 |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology
Type of heat pump | Air to Water |  | Source from Ecodesign Data or HARP Database or in compliance with DEAP methodology
Temperature Control (refered to as Capacity Control in Ecodesign Standard Template) | Variable Outlet |  | Source from Ecodesign Data
Does the installation provide: | Space heating and Domestic Hot Water |  | Source from Designer/ Installer sign off sheet or site evidence without Ecodesign
Space Heating Test Standard | I.S. EN 14825 |  | Source from Ecodesign Data or HARP Database
Water Heating Test Standard | I.S. EN 16147 |  | Source from Ecodesign Data or HARP Database
Operation Limit Temperature (TOL) | -20 | oC | Source from Ecodesign Data |  |  |  |  | Note: have deleted Row 31 as this is dealt with in the calcs on heating calc (row 38)
Heating water operating limit temperature (WTOL) | 60 | oC | Source from Ecodesign Data
5. Heating
Annual space heating requirement taken from DEAP |  | kWh | Source from the Distribution system loss and gains tab in DEAP
Is there a fixed secondary heater present? | No |  | Details on CHP and secondary heating must match the DEAP energy requirements entries.
Is there a CHP present? | No |  | Details on CHP and secondary heating must match the DEAP energy requirements entries.
Fraction of main space and water heating from CHP | 0.1 |  | Details on CHP and secondary heating must match the DEAP energy requirements entries.
Annual space heating provided by Heat Pump |  | kWh
Design Outdoor Temperature | -3 | oC | Based on CIBSE Guide A Section 2
Indoor Design Temperature (Mean Internal Temperature) | 18.24 | oC | Source from Net Space Heat Demand "Required mean internal temperature during heating hours degC"
Heat emission type served by heat pump within the dwelling: | Select all that apply:
1 or more Radiators | No
1 or more Fan Coil Units | No |  | Default Supply Temperature
Underfloor Heating | Yes |  | 35 | oC | Based on SAP input parameters.
Air used as Emitter (to Air Units) | No
Design Flow Temperature Use "Default Supply Temperature" unless other evidence available | 35 | oC
Exponent n, characterising type of emission system | 1.2 |  | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Emitter Temperature Drop | 5 | oC | Source from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps
Return Temperature at design conditions | 30
No of Hrs per Day Heat Pump in Operation | 24 | hrs | Source from Designer/ Installer sign off sheet, default is DEAP heating schedule which is 8 hrs a day
Cut-out hours | 0
Electricity Primary Energy Factor | 2.19 |  | Source from DEAP tool, Options
Is a Back Up Space Heater Present within Dwelling | Yes |  | Source from Designer/ Installer sign off sheet
Back Up Space Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Space Heater | 2.19
Efficiency of Back up Space Heater | 100% | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Space Heater relative to Direct Electric Heating | 1
Is there a water heater installed as back up for the heat pump | No |  | Source from Designer/ Installer sign off sheet
Back Up Water Heater Fuel | Electricity |  | Source from Designer/ Installer sign off sheet
Primary Energy Factor for Back Up Water Heater | 2.19
Efficiency of Back up Water Heater | 100% | % | Based on DEAP Methodology, defaults taken from DEAP Manual.
Adjusted Efficiency of Back up Water Heater relative to Direct Electric Heating | 1
6. Domestic Hot Water
Output from Main Water Heater |  | kWh/yr | Source from the Water Heating Tab, Output from Main Water Heater in DEAP
Type of DHW | Separate Hot Water Storage |  | An Integral Hot Water Store forms part of the Heat Pump, refer to DEAP Heat Pump Methodology for guidance.
Annual water heating provided by main water heating system |  | kWh/yr
Cold Water Inlet Temperature | 10 | oC | Based on DEAP Methodology
Required Flow Temperature from Heat Pump to Hot Water Storage | 65 | oC | Based on DEAP Methodology and guidelines for prevention of Legionella. Where the store is separate to the heat pump a 5oC drop is assumed.
Volume of DHW Storage | 209 | litres | Source from the Water Heating Tab, Storage in DEAP
7. Product Performance Data
Test Conditions EN 14825:2013 | High Temperature Data is mandatory requirement under Ecodesign Directive (Note its referred to as Medium Temperature Application in Ecodesign directive) |  | Source from Ecodesign Data or accredited tests to EN14825
Additional Test Points available at: | Low Temperature | Yes | Source from Ecodesign Data or accredited tests to EN14825
| Medium Temperature | No | Source from Ecodesign Data or accredited tests to EN14825
| Very High Temperature | No | Source from Ecodesign Data or accredited tests to EN14825
| Maximum Test Temperature allowed for in EN14825 testing | 55
| Test Conditions EN 14825:2013 | A (88%) -7oC | B (54%) 2oC | C (35%) 7oC | D (15%) 12oC | E* (100%) TOL
Low Temperature Application (35oC) | Source | A-7 | A2 | A7 | A12 | A-20
| Sink | W34 | W30 | W27 | W24 | W35
EN 14825:2013 - Table 12 (ASHP) or Table 24 (GSHP) | Heating Capacity (kW) | 6.04 | 3.67 | 4.36 | 4.17 | 5.41
| Coefficient of Performance (kW/kW) | 3.07 | 4.35 | 5.7 | 7.17 | 2.62
Mid Temperature Application (45oC) | Source | A-7 | A2 | A7 | A12 | A-20
| Sink | W43 | W37 | W33 | W28 | W45
EN 14825:2013 -Table 15 (ASHP) or Table 27 (GSHP) | Heating Capacity (kW) | 7 | 4.4 | 2.8 | 2.9 | 6.1
| Coefficient of Performance (kW/kW) | 1.95 | 3.14 | 4.63 | 6.17 | 1.71
High Temperature Application (55oC) | Source | A-7 | A2 | A7 | A12 | A-20
| Sink | W52 | W42 | W36 | W30 | W55
EN 14825:2013 - Table 6 (AAHP), Table 9 (GAHP), Table 18 (ASHP) or Table 30 (GSHP) | Heating Capacity (kW) | 5.67 | 3.53 | 4.14 | 4.01 | 5.38
| Coefficient of Performance (kW/kW) | 2.15 | 3.1 | 4.26 | 5.72 | 1.99
Very High Temperature Application (65oC) | Source | A-7 | A2 | A7 | A12 | A-20
| Sink | W61 | W49 | W41 | W32 | W65
EN 14825:2013 - Table 21 (ASHP) or Table 33 (GSHP) | Heating Capacity (kW) | 0 | 0 | 0 | 0 | 0
| Coefficient of Performance (kW/kW) | 0 | 0 | 0 | 0 | 0
Test Conditions EN 14511-2
Is the Heat Pump Listed on HARP | Yes
Enter SPF based on DEAP Methodology/ HARP | 0 | kW/kW | Derive SPF from HARP, certified data COPs in compliance with DEAP methodology or from DEAP table 4a defaults
Is there load or weather compensation present? | Yes |  | Source from Designer/ Installer sign off sheet or site evidence
Does the heat pump have an Integral Immersion | No |  | Source from Designer/ Installer sign off sheet or site evidence
Does heat pump reach a flow temperature of >=65oC | No |  | Source from CE marked literature, CE marked dataplates or accredited test data for the heat pump in question.
Test Conditions EN 16147
Source of data | Water heating energy efficiency, ηwh |  | Source from Ecodesign Data or accredited tests to EN 16147
Water heating energy efficiency, ηwh | 119 | % | Source from Ecodesign Data or accredited tests to EN 16147
Equivalent Coefficient of Performance | 2.975 | kW/kW
Reference Hot Water Temperature | 55 | oC | Source from Ecodesign Data or accredited tests to EN 16147, set at 40oC if unknown.
Required Source Temperature | 7 | oC | Based on Table 5 of EN 16147
Capacity of Heat Pump | 6.41 | kW | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147
Declared Load Profile | L |  | Source from Ecodesign Data, manufacturers data or accredited tests to EN 16147
Standby Heat Loss | 1.2 | kWh/day | Source from Ecodesign Data or accredited tests to EN 16147, set as 0 if unknown
Volume of DHW accounted for in test | 209 | litre | Source from Ecodesign Data or accredited tests to EN 16147
Test Conditions EN 255-3
Coefficient of Performance | 0 | kW/kW | Source from accredited test data certificate
Reference Hot Water Temperature | 0 | oC | Source from accredited test data certificate, set at 40oC if unknown.
Heating Capacity DHW | 0 | kW | Source from accredited test data certificate
8. Results
Results
Efficiency of Main Heating System | #VALUE! | % | Enter this in DEAP: energy requirements: space heating
Efficiency Adjustment Factor - Main Heating | 1 |  | Enter this in DEAP: energy requirements: space heating
Efficiency of Main Hot Water System | #VALUE! | % | Enter this in DEAP: energy requirements: water heating
Efficiency Adjustment Factor - Main Hot Water | 1 |  | Enter this in DEAP: energy requirements: water heating
Additional Renewable Contribution from Heat Pump | 0 | kWh/year | Enter this in DEAP: energy requirements: fuel data: Renewable Energy: Energy Saved or Produced: Renewable Thermal: Part L Total contribution (kWh/yr). Note: this is only applied to Part L renewable contribution in new dwelling assessments.
Colour Key
User Input, only editable cells
Calculated Value
Constant
User does not need to edit,
based on previous inputs

## Heating Calc
EN 15316 methodology |  | Bin 1 | Bin 2 | Bin 3 | Bin 4 | Bin 5 | Total | Guidance Note |  |  |  | Back Up Heating |  |  |  |  | #VALUE! | #VALUE! | [5 empty] | #VALUE!
Bin Data | I.S. EN 14825 Test Conditions | (E) 100% | (A) 88% | (B) 54% | (c) 35% | (D)15%
Operating Points (Bin Temperatures) | Test Points | -20 | -7 | 2 | 7 | 12 |  | Taken from IS EN 14825 standard |  | TOL | kW | Outdoor temperature bin (deg C) | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8 | Bin Time (h) | Effective Bin Time (h) | Energy to be produced for SH (kWh) | Energy to be produced for DHW (kWh) | Energy Required from Heat Pump (kWh) | Supply Flow Temp oC…B1 | Heating Capacity kW…As per D12 and MCS Tool* (see below) | Required Running Hours (hr) Eqt 28 | Diff between Required Running Hrs and Effective Bin..Eqt 40 | SAP Methodology Back Up Heater based on Plant Size Ratio | Energy Required from back up (kWh)…Eqt 40 | Total Back Up Heater | SAP Methodology - Table N9
Lower Limit (oC ) | Mid Test Points | -12 | -13.5 | -2.5 | 4.5 | 9.5 |  | For Bin 1, the Lower Limit is the Lowest Outdoor Temperature as per D.1.3.2.1 |  | -20 | 5.3935 | -12 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 40.9408 | 5.7448 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Plant Size Ratio | 24 | 16 | 11
Upper Limit, (oC ) | Mid Test Points | -13.5 | -2.5 | 4.5 | 9.5 | 35 |  | For Bin 5, the Upper Limit is the Upper Outdoor Temperature as per D.1.3.2.1 |  |  |  | -11 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 40.2941 | 5.7888 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.2 | 0.4 | 0.53 | 0.64
Source Temperature (oC) |  | -20 | -7 | 2 | 7 | 12 | [5 empty] | -10 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 39.6445 | 5.8327 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.25 | 0.28 | 0.43 | 0.57
Weighting Factor SH | Eqt 4 | 0 | 0.005882 | 0.30194 | 0.46292 | 0.22926 | 1 |  |  |  |  | -9 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 38.9916 | 5.8766 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.3 | 0.19 | 0.34 | 0.49
Space Heating Energy (kWh) | Eqt 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  |  | -8 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 38.3355 | 5.9205 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.35 | 0.12 | 0.27 | 0.42
Bin Time (h) | Eqt 6 | 0 | 18 | 1247 | 2933 | 4562 | 8760 |  |  |  |  | -7 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 37.6759 | 5.9644 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.4 | 0.06 | 0.2 | 0.35
Effective Bin Time (h) | Eqt 7 | 0 | 18 | 1247 | 2933 | 4562 | 8760 |  |  |  |  | -6 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 37.0128 | 5.7075 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.45 | 0.03 | 0.14 | 0.29
Weighting Factor DHW | Eqt 8 | 0 | 0.0020548 | 0.14235 | 0.33482 | 0.52078 | 1 |  |  |  |  | -5 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 36.3459 | 5.4505 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.5 | 0.01 | 0.09 | 0.24
DHW Energy (kWh) | Eqt 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  |  |  | -4 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 35.675 | 5.1936 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.55 | 0 | 0.06 | 0.19
[12 empty] | -3 | 0.0013629 | 0.00045662 | 4 | 4 | #VALUE! | #VALUE! | #VALUE! | 35 | 4.9366 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.6 | 0 | 0.03 | 0.15
Test Data |  | -20 | -7 | 2 | 7 | 12 | [5 empty] | -2 | 0.0045191 | 0.0015982 | 14 | 14 | #VALUE! | #VALUE! | #VALUE! | 34.3206 | 4.6797 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.65 | 0 | 0.02 | 0.11
Low Temperature (oC ) | Taken from EN 14825 test data | 35 | 34 | 30 | 27 | 24 | [5 empty] | -1 | 0.013414 | 0.0050228 | 44 | 44 | #VALUE! | #VALUE! | #VALUE! | 33.6365 | 4.4227 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.7 | 0 | 0.01 | 0.09
Medium Temperature (oC ) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0.032136 | 0.012785 | 112 | 112 | #VALUE! | #VALUE! | #VALUE! | 32.9475 | 4.1658 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.75 | 0 | 0 | 0.05
High Temperature (oC ) | Taken from EN 14825 test data | 55 | 52 | 42 | 36 | 30 | [5 empty] | 1 | 0.039273 | 0.016667 | 146 | 146 | #VALUE! | #VALUE! | #VALUE! | 32.2533 | 3.9088 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.8 | 0 | 0 | 0.05
Very High Temperature (oC ) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 | [5 empty] | 2 | 0.055736 | 0.025342 | 222 | 222 | #VALUE! | #VALUE! | #VALUE! | 31.5534 | 3.6519 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.85 | 0 | 0 | 0.03
COP at sink temperature Low Temp (kW/kW) | Taken from EN 14825 test data | 2.62 | 3.07 | 4.35 | 5.7 | 7.17 |  | Taken from Input Sheet Low Temperature COP |  |  |  | 3 | 0.075301 | 0.036872 | 323 | 323 | #VALUE! | #VALUE! | #VALUE! | 30.8476 | 3.7888 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.9 | 0 | 0 | 0.02
COP at sink temperature Medium Temp (kW/kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Medium Temperature COP |  |  |  | 4 | 0.086079 | 0.045662 | 400 | 400 | #VALUE! | #VALUE! | #VALUE! | 30.1353 | 3.9258 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.95 | 0 | 0 | 0.01
COP at sink temperature High Temp (kW/kW) | Taken from EN 14825 test data | 1.99 | 2.15 | 3.1 | 4.26 | 5.72 |  | Taken from Input Sheet High Temperature COP |  |  |  | 5 | 0.087979 | 0.050913 | 446 | 446 | #VALUE! | #VALUE! | #VALUE! | 29.4159 | 4.0628 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1 | 0 | 0 | 0.01
COP at sink temperature Very High Temp (kW/kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Very Temperature COP |  |  |  | 6 | 0.097735 | 0.062215 | 545 | 545 | #VALUE! | #VALUE! | #VALUE! | 28.689 | 4.1997 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.05 | 0 | 0 | 0
Heating Capacity at Low Temp (kW) | Taken from EN 14825 test data | 5.41 | 6.04 | 3.67 | 4.36 | 4.17 |  | Taken from Input Sheet Low Temperature Capacity |  |  |  | 7 | 0.097323 | 0.068836 | 603 | 603 | #VALUE! | #VALUE! | #VALUE! | 27.9536 | 4.3367 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Heating Capacity at Medium Temp (kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Medium Temperature Capacity |  |  |  | 8 | 0.0944 | 0.075114 | 658 | 658 | #VALUE! | #VALUE! | #VALUE! | 27.2091 | 4.3028 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
Heating Capacity at High Temp (kW) | Taken from EN 14825 test data | 5.38 | 5.67 | 3.53 | 4.14 | 4.01 |  | Taken from Input Sheet High Temperature Capacity |  |  |  | 9 | 0.085487 | 0.07774 | 681 | 681 | #VALUE! | #VALUE! | #VALUE! | 26.4542 | 4.2688 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Heating Capacity at Very High Temp (kW) | Taken from EN 14825 test data | 0 | 0 | 0 | 0 | 0 |  | Taken from Input Sheet Very Temperature Capacity |  |  |  | 10 | 0.068755 | 0.072945 | 639 | 639 | #VALUE! | #VALUE! | #VALUE! | 25.6877 | 4.2349 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[12 empty] | 11 | 0.059179 | 0.075342 | 660 | 660 | #VALUE! | #VALUE! | #VALUE! | 24.9079 | 4.2009 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Appropriate Test Data | Lower Test Points | Low | [9 empty] | 12 | 0.043757 | 0.069635 | 610 | 610 | #VALUE! | #VALUE! | #VALUE! | 24.1127 | 4.167 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| Higher Test Points | High | [9 empty] | 13 | 0.031311 | 0.066438 | 582 | 582 | #VALUE! | #VALUE! | #VALUE! | 23.299 | 4.1331 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| To Air Heat Pump | No | [9 empty] | 14 | 0.017252 | 0.054909 | 481 | 481 | #VALUE! | #VALUE! | #VALUE! | 22.4627 | 4.0991 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Lower Test Points - Temperature (oC) | Low | 35 | 34 | 30 | 27 | 24 | [5 empty] | 15 | 0.0090024 | 0.057306 | 502 | 502 | #VALUE! | #VALUE! | #VALUE! | 21.5972 | 4.0652 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Higher Test Points - Temperature (oC ) | High | 55 | 52 | 42 | 36 | 30 | [5 empty] | 16 |  | 0.043721 | 383 | 383 |  | #VALUE! | #VALUE!
Lower Test Points - COP (kWh/kWh) | Low | 2.62 | 3.07 | 4.35 | 5.7 | 7.17 | [5 empty] | 17 |  | 0.029566 | 259 | 259 |  | #VALUE! | #VALUE!
Higher Test Points - COP (kWh/kWh) | High | 1.99 | 2.15 | 3.1 | 4.26 | 5.72 | [5 empty] | 18 |  | 0.019406 | 170 | 170 |  | #VALUE! | #VALUE!
Lower Test Points - Heating Capacity (kW) | Low | 5.41 | 6.04 | 3.67 | 4.36 | 4.17 | [5 empty] | 19 |  | 0.012785 | 112 | 112 |  | #VALUE! | #VALUE!
Higher Test Points - Heating Capacity (kW) | High | 5.38 | 5.67 | 3.53 | 4.14 | 4.01 | [5 empty] | 20 |  | 0.0076484 | 67 | 67 |  | #VALUE! | #VALUE! |  | * Interpolation equation as per EN 15316, however using same methodology as MCS tool as single point data may ony be available
Supply Flow Temperature based on Single Test Points | Equation B1 - Based on 55oC only | 78.6639 | 60.7687 | 47.545 | 39.7217 | 31.3191 |  | Supply Flow Temperature based on 55oC, to meet the mandatory test points in Ecodesign, to use for single test point data |  |  |  | 21 |  | 0.0042237 | 37 | 37 |  | #VALUE! | #VALUE!
Source Temperature | Section F2.1 | -20 | -7 | 2 | 7 | 12 | [5 empty] | 22 |  | 0.0030822 | 27 | 27 |  | #VALUE! | #VALUE!
Supply Flow Temperature | Equation B1 | 46.0177 | 37.6759 | 31.5534 | 27.9536 | 24.1127 | [5 empty] | 23 |  | 0.0022831 | 20 | 20 |  | #VALUE! | #VALUE!
Heating Capacity for Source Temp | Section 5.3.5.1.3 | Not applicable, for water and exhaust heat pumps the source temperature is constant, for air heat pumps we have test data at various conditions and for brine heat pumps as we don't have different source temperatures it is not possible to carry out interpolation. | [9 empty] | 24 |  | 0.001484 | 13 | 13 |  | #VALUE! | #VALUE!
Heating Capacity for Supply Temp | Linear Interpolation (5.3.5.1.3) (Eqt D12) | 5.3935 | 5.9644 | 3.6519 | 4.3367 | 4.167 |  | Refer to Heating Capacity calculated for each external temperature as per Column W. Note: As per Annex D, heating capacity cannot be adjusted for single test points |  |  |  | 25 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
[12 empty] | 26 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Standard Rating Conditions | Based on EN 14511 | 3.67 | kW |  |  |  |  | In EN 14825, the water flow rate is determined according to EN 14511 at standard rating conditions. |  |  |  | 27 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Mass Flow Rate | kg/s, Equation 10 | 0.17551 | [5 empty] | 5K is based on EN14511 for electrically driven heat pumps, 4.182 kJ/kg/K is the specific heat capacity of water. |  |  |  | 28 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Temp Spread at Lower Temp | oC, Equation 10 | 7.3706 | 8.2289 | 5 | 5.9401 | 5.6812 | [5 empty] | 29 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Temp Spread at Higher Temp | oC, Equation 10 | 7.3297 | 7.7248 | 4.8093 | 5.6403 | 5.4632 | [5 empty] | 30 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Required Heating Capacity at design conditions | Taken from DEAP | #VALUE! | kW |  |  |  |  | PSR | #VALUE! |  |  | 31 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Delta T for emitter | Taken from Input | 5 | [9 empty] | 32 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Required Mass flow at design conditions | kg/s, Equation 10 | #VALUE! | [9 empty] | 33 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Temp Spread at Lower Temp Test Points at design conditions | oC, Equation 10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | 34 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Temp Spread at Higher Temp Test Points at design conditions | oC, Equation 10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | 35 |  | 0 | 0 | 0 |  | #VALUE! | #VALUE!
Correction Factor COP Lower Temp Test Points | eqt 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Correction Factor COP Higher Temp Test Points | eqt 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
COP corrected for Lower Temp | eqt 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
COP corrected for Higher Temp | eqt 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Interpolation of COP | Linear Interpolation (5.3.5.1.3), refer to Eqt D11 Single Point eqt C5/C6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | For Single set of test points, the COP is based on adjustment in Annex C and is based on Supply Temp of 55oC, to meet the mandatory test results for Ecodesign. As outlined in Annex C, accuracy deteriorates with increasing distance from test points therefore methodology not used for Fixed Outlet
Storage Losses |  | Buffer Vessels for space heating only excluded, as per other systems in DEAP
Space Heating Energy Requirement | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy to be produced by back up heater for Space Heating only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy Provided by Backup Space Heater for Space Heating Only | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | For non electric back up heaters this has been converted to equivalent electric energy using Bivalent system
Back Up for Temperature Increase not included as test data for higher temperatures must be provided.
Auxiliary Energy for central heating pumps & DHW pumps excluded as allowed for in DEAP
Recoverable heat from auxiliary energy (pumps) and thermal losses (storage) excluded as allowed for in DEAP
Electrical Energy for Space Heating from heat pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Total Electrical Energy Required | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump & Back up Heater | [6 empty] | #VALUE!
Renewable Contribution calculated in DEAP | [6 empty] | #VALUE! | kWh
Space Heating Provided by Heat Pump | kWh | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
SPF - Heat Pump only | [6 empty] | #VALUE!
Renewable Contribution provided by Heat Pump | [6 empty] | #VALUE! | kWh
Additional Renewable Contribution from Heat Pump | [6 empty] | 0 | kWh

## DHW Calc
From Ecodesign / 814
EN 16147 |  |  |  | Tapping Cycle | kWh/day |  | Test Check | Installed Check | Error - Test | Error - Dwelling
Volume of Tank in Test | 209 |  | based on test data | 3XS | 0.345 | 7 |  |  | 0 | 0
Average Storage Temperature | 65 | oC |  | XXS | 2.1 | 15 |  |  | 0 | 0
Standby Heat loss | 1.2 | kWh/day | based on test data | XS | 2.1 | 15 |  |  | 0 | 0
Declared Load Profile | L |  |  | S | 2.1 | 36 |  |  | 0 | 0
Min Volume for cycle | 130 | litre |  | M | 5.845 | 65 | 43.3333 | 39 | 0 | 0
DHW Demand based on Cycle | 11.655 | kWh/day | based on default for Cycle | L | 11.655 | 130 | 86.6667 | 78 | 0 | 0
COP based on EN 16147 | 2.975 |  |  | XL | 19.07 | 210 | 140 | 126 | 0 | 0
Capacity of Heat Pump | 6.41 | kW |  | XXL | 24.53 | 300 | 200 | 180 | 0 | 0
|  |  |  | 3XL | 46.76 | 520 | 346.6667 | 312 | 0 | 0
Efficiency for DEAP | 3.2813 |  | based on equation from SAP 2009 & 2012 - Calculation Methodology for electrically driven heat pumps, converting 15316-4-2:2008 SPF to SAP SPF | 4XL | 93.52 | 1040 | 693.3333 | 624 | 0 | 0
0
Reference Temperature | 55 | oC | [6 empty] | 0 | 0
Temperature of DHW | 65 | oC
Temperature of Cold Water Inlet | 10 | oC | [6 empty] | WARNING: The Test Storage Volume does not meet requirements in Ecodesign Directive, the assessor must contact the manufacturer to advise that test volume is not appropriate for the declared load profile and request revised test results. | WARNING: The test data is not appropriate for the installation within the dwelling, the assessor must contact the client/ designer and installer, advising that the installed hot water cylinder is not appropriate for the Ecodesign Directive efficiency data and therefore the heat pump will not perform to the same efficiency.
Fraction of Demand met by backup energy to meet temperature shortfall | 0.18182 |  | based on eqt 18 from EN 15316
DHW Demand for Dwelling |  | kWh
Required Running Hours | #VALUE! | hrs
Effective Bin Time | 8760 | hrs | based on eqt 7 from EN 15316
Difference between Req and Effective | #VALUE!
Fraction of Demand met by backup to meet operation hours shortfall | #VALUE!
Heat Pump Electricity | #VALUE! | kWh
Back Up Heater due to temperature shortfall | #VALUE! | kWh | Efficiency of Back up Water Heater adjusted relative to Direct Electric Heating
Back Up Heater due to operation shortfall | #VALUE! | kWh | Efficiency of Back up Water Heater adjusted relative to Direct Electric Heating
Total Electricity Required for Water Heating | #VALUE! | kWh
SPF | #VALUE!
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
SPF - Heat Pump Only | #VALUE!
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
Additional Renewable Contribution from Heat Pump | 0 | kWh
EN 255-3
DHW Demand for Dwelling |  | kWh
COP based on EN 255 | 0
Capacity of Heat Pump | 0 | kW
Reference Temperature | 0 | oC
Temperature of DHW | 65 | oC
Temperature of Cold Water Inlet | 10 | oC
Fraction of Backup energy due to temperature shortfall | 1.1818 |  | based on eqt 18 from EN 15316
Electricity required by Heat Pump | #VALUE! | kWh
Electricity required by Back Up Heater | #VALUE! | kWh
Total Electricity Required for Water Heating | #VALUE! | kWh
SPF | #VALUE!
Renewable Contribution calculated in DEAP | #VALUE! | kWh
Hot Water Provided by Heat Pump | #VALUE! | kWh
SPF - Heat Pump Only | #VALUE!
Renewable Contribution provided by Heat Pump | #VALUE! | kWh
Additional Renewable Contribution from Heat Pump | 0 | kWh
EN 14511
DHW Demand for Dwelling |  | kWh
COP based on EN 14511 | 0
Efficiency Adjustment Factor | 1
SPF | #DIV/0!
Total Electricity Required for Water Heating | #VALUE! | kWh
Renewable Contribution calculated in DEAP | #DIV/0! | kWh
Hot Water Provided by Heat Pump | #DIV/0! | kWh
Electricity required by Heat Pump | #DIV/0! | kWh
Renewable Contribution provided by Heat Pump | 0 | kWh
Additional Renewable Contribution from Heat Pump | 0 | kWh

## Meteorological data
| 16 | Design Temperature |  |  |  | DHW Energy kWh
Taken as 16 based on EN14825
Outdoor temperature bin (deg C) | Name IRL_Dublin_IWEC2.epw Description IWEC2- ASHRAE Latitude 53.43000031 Longitude -6.25 Time Zone -0.419999987 Year 2000 Ground Source Temperature 11.97182465 Altitude 0 Number of hours per bin | Cumulative Hrs | Heating Degree Hrs | Cumulative heating Degree Hrs | Heating Weighting Factor…Eqt 4 | DHW Weighting Factor…Eqt 8
-12 | 0 | 0 | 0 | 0 | 0 | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0
-5 | 0 | 0 | 0 | 0 | 0 | 0
-4 | 0 | 0 | 0 | 0 | 0 | 0
-3 | 4 | 4 | 76 | 76 | 0.0013629 | 0.00045662
-2 | 14 | 18 | 252 | 328 | 0.0045191 | 0.0015982
-1 | 44 | 62 | 748 | 1076 | 0.013414 | 0.0050228
0 | 112 | 174 | 1792 | 2868 | 0.032136 | 0.012785
1 | 146 | 320 | 2190 | 5058 | 0.039273 | 0.016667
2 | 222 | 542 | 3108 | 8166 | 0.055736 | 0.025342
3 | 323 | 865 | 4199 | 12365 | 0.075301 | 0.036872
4 | 400 | 1265 | 4800 | 17165 | 0.086079 | 0.045662
5 | 446 | 1711 | 4906 | 22071 | 0.087979 | 0.050913
6 | 545 | 2256 | 5450 | 27521 | 0.097735 | 0.062215
7 | 603 | 2859 | 5427 | 32948 | 0.097323 | 0.068836
8 | 658 | 3517 | 5264 | 38212 | 0.0944 | 0.075114
9 | 681 | 4198 | 4767 | 42979 | 0.085487 | 0.07774
10 | 639 | 4837 | 3834 | 46813 | 0.068755 | 0.072945
11 | 660 | 5497 | 3300 | 50113 | 0.059179 | 0.075342
12 | 610 | 6107 | 2440 | 52553 | 0.043757 | 0.069635
13 | 582 | 6689 | 1746 | 54299 | 0.031311 | 0.066438
14 | 481 | 7170 | 962 | 55261 | 0.017252 | 0.054909
15 | 502 | 7672 | 502 | 55763 | 0.0090024 | 0.057306
16 | 383 | 8055 | 0 |  |  | 0.043721
17 | 259 | 8314 |  |  |  | 0.029566
18 | 170 | 8484 |  |  |  | 0.019406
19 | 112 | 8596 |  |  |  | 0.012785
20 | 67 | 8663 |  |  |  | 0.0076484
21 | 37 | 8700 |  |  |  | 0.0042237
22 | 27 | 8727 |  |  |  | 0.0030822
23 | 20 | 8747 |  |  |  | 0.0022831
24 | 13 | 8760 |  |  |  | 0.001484
25 | 0 | 8760 |  |  |  | 0
26 | 0 | 8760 |  |  |  | 0
27 | 0 | 8760 |  |  |  | 0
28 | 0 | 8760 |  |  |  | 0
29 | 0 | 8760 |  |  |  | 0
30 | 0 | 8760 |  |  |  | 0
31 | 0 | 8760 |  |  |  | 0
32 | 0 | 8760 |  |  |  | 0
33 | 0 | 8760 |  |  |  | 0
34 | 0 | 8760 |  |  |  | 0
35 | 0 | 8760 |  |  |  | 0
0